## Sheet1
Maintenance Use Only
ASSET NO. (IF TAGGED) | CAMPUS | BUILDING | FLOOR | ROOM NO./DESCRIPTION | ASSET DESCRIPTION (include areas served, associated assets | PHOTO REFERENCE NO(S). (ATTACH PHOTO TO EMAIL, FORMATS JPG, JPEG, PNG, GIF, TIF, TIFF, SVG, BMP, ICO ONLY | COMMENTS / SYSTEM OPERATION/ REFRIGERANT | BUSINESS CRITICAL? | STATUTORY? | CBS/CL3 ASSET? | MANUFACTURER | MODEL | SERIAL NO | DATE INSTALLED | ASSET GROUP CLASSIFICATION REF | ASSET GROUP CLASSIFICATION DESCRIPTION | ASSET CONDITION - CIBSE GRADE | IS PPM REQUIRED? | PPM FREQUENCY | START DATE | SFG20 REF/INSTRUCTION SET (WHAT NEEDS TO BE DONE) | CONTRACT / WHO DOES THE WORK?
ICL025190 | SK | Roderic Hill | Roof | Roof West | Chiller – Carrier 160Kw serving offices on level 4 to 6 | IMG_2927.jpg |  |  |  |  | Carrier | 30RBS-160C0145-PE | M2018013808 |  | D.05.02.07 | Packaged Chiller Unit | B | Y | 3/6/12M |  | 09-02 | CHILL
Note on V93: Patel, Rakesh: Drinking Water Sentinels Basement Kitchen 4th level kitchen Cold water sentinels CWS1 Ground level Lab G6A 3rd level Lab 5 CWS2 3rd level Gents WC Basement level Gents
Note on V94: Patel, Rakesh: Monitor and test each water heater monthly. Please see water risk assessment for further details
Note on V95: Patel, Rakesh: Samples should be collected annually as indicated below 2x Legionella samples from the far points of the cold water systems. 4x Legionella samples from the hot water heater supply (this will take into account the flexihose and expansion vessel effect on the water system. 1x TVC/Coliform/E.Coli sample, Drinking water sample from 4th level kitchen 1x TVC/Coliform/E.Coli sample, from CWS1 1x TVC/Coliform/E.Coli sample, from CWS2
Note on V237: Patel, Rakesh: Filters must be changed 6 monthly to prevent bacterial contamination. All change over must be recorded in a logbook
Note on V238: Patel, Rakesh: Filters must be changed 6 monthly to prevent bacterial contamination. All change over must be recorded in a logbook
Note on V239: Patel, Rakesh: Filters must be changed 6 monthly to prevent bacterial contamination. All change over must be recorded in a logbook